RUG3 SPECIFICATION, v 1.91

# REMOTE TERMINAL UNITS

## OVERVIEW

The remote controllers shall be fully integrated microprocessor based units specifically designed for unattended operation in unconditioned environments having wide temperature ranges, wide humidity ranges, high electrical noise, high audible noise and high vibration.  They shall include surge protected analog, digital and communications interfaces to interface directly with all standard transducers, actuators, and communications equipment without the need for intervening conditioning devices.  An integral operator interface shall be provided such that normal operations such as device enabling/disabling, on/off control, mode changes, setpoint changes, etc. shall be accomplished with English language prompting and shall not require any programming, command code memorization, or reference to any operating instructions.  The units shall require no cooling fans and shall be resistant to dust, water and insects.

## GENERAL ARRANGEMENT

Each RTU shall consist of a single circuit card with I/O as required by the I/O functional requirements.  The card shall be housed in a powder coated 16 gauge steel case with integral keyboard and LCD display.  The RTU shall be panel mountable with a sealable front plate requiring no more than two fasteners necessary to mount the entire unit.  It shall be available as backpan mountable on DIN rail, requiring no tools to either mount or dismount the unit.  I/O connections shall use rising cage clamp type screw terminals in multi-screw housings that are removable without removing individual wires.  Screw housings shall have different numbers of terminals so the proper locations cannot be confused.  The card cage shall be powered by nominal 12 VAC or 12-15 VDC.

## PROGRAMMING

The RTU shall not require procedural programming in the usual sense.  Instead, the unit shall be equipped with pre-programmed modules enabling the programmer to configure the unit using a manufacturer supplied Windows compatible support software program.  With that program, the programmer shall be able to design his control strategies, displays, telemetry formats, etc. by interconnecting the pre-programmed modules using a technique of pointing, clicking and dragging on the Windows screens.  He shall then command the support software to send the configuration file to the RTU, where it shall begin running automatically.

## SUPPORT SOFTWARE

Support software shall be Windows 95/98/2000/ME/NT/XP compatible.  The software shall be self-contained and complete in that it shall not require any equipment or software other than Windows running on a PC along with a serial cable or USB cable to define the RTU program and load it into the RTU and start it running.  It shall enable the programmer to configure the unit by identifying and naming pre-programmed modules for installation into the overall control strategy without the need for any procedural programming.

## SUPPORT SOFTWARE UPGRADES

The latest support software revision shall be available at any time from the manufacturer’s web site for download at no charge.  No registration, product code or password shall be required to obtain any revision.

## OPERATING SYSTEM UPGRADES

The RTU operating system (OS) shall be contained in flash memory in the RTU.  It shall be reloadable serially from the support software.  The RTU OS shall be included with the support software and shall be available from the manufacturer’s web site for download at no charge.  No registration, product code or password shall be required to obtain any OS revision.

## SUPPORT HARDWARE

The RTU shall not require any support hardware other than a power supply and a serial cable for loading and running programs.  Special hardware such as special purpose programming panels or dongles shall not be required.

# RTU ELECTRONIC CHARACTERISTICS

Units shall be designed to operate reliably in high electrical noise, wide temperature range environments without external cooling or noise suppression equipment.  All components and subassemblies shall be new and of recent manufacture.  The design shall be conservative in that all components shall operate at no more than 50% of rated thermal dissipation in worst case conditions.  There shall be 30% timing margin in all critical timing paths.

## LOGIC FAMILY

Unit electronics shall be constructed entirely using the high noise immunity, low power CMOS logic family.  No NMOS, TTL or bipolar components shall be used.

## MICROPROCESSOR

The microprocessor shall be a 16 bit pipelined design that shall employ a 16 bit address bus and 16 bit data bus.  The microprocessor shall include a watchdog timer, autobooting reset circuitry, multiple crystal controlled oscillators, oscillator stability determination and failsafe mode, low power battery backup capability, and other features necessary to assure operation in conditions of intermittent or sagging power.

## MEMORY

### FLASH

Electrically erasable programmable FLASH memory shall be employed to contain the operating system, background scanning software, communications software, calibration constants and all software specifically written and installed for this project.  No batteries shall be required to maintain the contents of this memory for up to 20 years of power outage.  The FLASH shall be partitioned to allow installation of the operating system as well as the application specific code without affecting any other FLASH contents.  Boot loader code shall be contained in a section of the FLASH that is protected from erasure other than at the factory.  A total of 60K bytes of contiguous FLASH memory shall be installed in each unit, which shall include at least 20% spare capacity in each of the boot loader, operating system and application areas.

### RAM

Static random access memory (RAM) shall be employed for data bases, communications buffers, and to store temporary variables, totalizations, logged data, and any other data specifically used for this project that changes momentarily.  A minimum of 2K bytes of contiguous battery backed up RAM shall be installed in each unit.  Lithium battery backup shall power the RAM for a minimum of 3 years of power outage cumulative over a 20 year period.

### Logging EEPROM

A minimum of 2 Mbytes of EEPROM shall be provided and used for storing logged data and time tags.  No batteries shall be required to maintain the contents of this memory for up to 20 years of power outage.  Preprogrammed software modules shall be supplied that implement convenient storage and retrieval of time tagged data points.

### WRITE PROTECTION

FLASH memory sectors allocated for operating system and user program storage shall be protected from writing whenever the program is running.  It shall also be protected for at least 1.7 seconds following power application, watchdog timer timeout, or brownout detection.  Boot loader program shall be protected from field alteration.

### BATTERY BACKUP

RAM memory and the realtime clock shall be powered during primary power outages by a lithium battery whose capacity over a 20 year period shall be sufficient to power the memory and clock for accumulated outages of at least 3 years.  It shall be possible for project personnel to replace the battery without the use of a soldering iron.

## DISPLAY

Each unit shall be equipped with a dot matrix type liquid crystal display (LCD) having at least 16 characters by 2 lines capacity.  With the display, it shall be possible to present values, statuses, engineering units, alarm messages, and prompts to project personnel.  The display shall provide the full ASCII character set.  Multiple display pages shall be possible, limited only by available flash memory capacity.  Each display shall consist of up to 50 lines of display presentation, visible two lines at a time by hitting up arrow and down arrow keys on the keyboard.  Display contrast shall be adjustable by key entry on the front panel keyboard or from the serial port on the CPU card.

## KEYBOARD

An integral numeric keyboard of at least 16 keys shall be provided for use by project personnel to change setpoints, acknowledge alarms, control devices, trigger events, and in general interact with the unit in a prompted English language dialogue that requires no memorization of command codes.  The keyboard shall be a sealed, membrane type with tactile feedback that shall be impervious to water or dust.  The keyboard shall have numeric keys so that key functions can be designated on the display for easy, one keystroke invocation.  As a minimum, the following keys shall be provided:

Numeric 0 to 9

(-) minus sign

(.) decimal point

Up arrow

Down arrow

ENTER

CLEAR

## REALTIME CLOCK/CALENDAR

A realtime clock/calendar shall be provided which shall provide the following time values:

Seconds	Day       	Day of week

Minutes        	Month

Hours          	Year

These values shall be available to the operating program for time-based event and report triggering, and logged data time tagging.  Software shall be provided for convenient and accurate time setting in English language format.  It shall also be able to set the clock from the telemetry channel for system wide clock synchronization purposes.  The clock shall have a rate accuracy of +/-.005%.  It shall include a lithium battery backup to assure clock running over accumulated power outages of at least 3 years over a 20 year period.

## OPERATIONAL SECURITY

### WATCHDOG TIMER

A hardware watchdog timer shall be provided that shall require correct operation of both the operating application program and background interrupt software.  The timer shall timeout and restart the program within 0.5 seconds of program failure.

### BROWNOUT DETECTOR

A hardware brownout detector shall detect sagging power or impending power loss and halt the processor in advance of loss of regulated power to assure orderly shutdown and restart in conditions of

fluctuating primary power.  It shall employ 10% hysteresis to eliminate the possibility of multiple restarts on power application.

### AUTOBOOTING

Upon power application or upon restarting after a watchdog timer timeout, the unit shall test the operating system and then test the application program.  If both are intact, the unit shall restart the application program.  If either is not intact, the operating system or boot loader shall prompt the user on the CPU serial port to reload the corrupted code.  There shall be no loss of memory, loss of temporary storage contents, or loss of clock/calendar function due to power outages of up to 3 years.

# I/O INTERFACES

## GENERAL OPTICAL ISOLATION AND SURGE PROTECTION

Each analog input, analog output and digital input shall be equipped with circuitry to protect the input from surges in accordance with IEEE surge withstand guidelines.  Additionally, analog inputs shall employ noise filters, current limiting resistors and zener clamps per channel to limit voltage excursion to within the A/D converter's operating range.  Digital outputs shall employ relays with minimum 2500 V coil to contact isolation.

## ANALOG INPUTS

Each unit shall provide 6 analog inputs for measuring external analog values from standard 4-20 ma or 0-5 VDC transducers.  Analog to digital conversion shall employ 12 bit successive approximation technique at a sample rate of 10 samples per second.  Inputs shall be individually software selectable as either 4-20 ma. current loop or 0 to 5 VDC voltage compatible.  In current loop mode, the input shall be able to measure down to zero milliamps.  Input impedance shall be nominal 220 ohms for current loop channels, and 20 kilohms for voltage channels.  Power shall not be taken from the analog signal.  Linearity, zero and full-scale error shall each be less than +/- 0.5 LSB over the range of -40 to+85 degrees C.  Reference temperature drift shall be less than 0.1 mv/deg.C.  Reference aging drift shall be less than 0.02 mv.  Over or under voltage inputs shall not effect other input measurement accuracy.  A/D conversion techniques such as integrating types that allow out of range inputs to effect other channels shall not be acceptable.  Background software shall sample the analog inputs continuously and hold raw values for use by the analog input modules.  The analog input modules shall apply low pass filtering and engineering units conversion as specified by the configuration file, and then transfer the samples to the floating point data base for use by other modules.  Each board shall hold factory calibration for both 4-20 ma and 0-5 V in onboard flash memory so that field calibration will be unnecessary.

### ANEMOMETER INPUT

One analog input on the board shall amplify, clip, digitize and count a nominal +/-

20 mv anemometer AC signal to obtain wind speed.

## DIGITAL INPUTS

Each board shall provide 8 self powered channels with a common return pin.  They shall be dry contact compatible using the onboard power supply.  Self powering voltage shall be 12 volts for high noise immunity.

### STANDARD DC DIGITAL INPUTS

Whenever the digital input is sampled by a DC digital input module, the returned state shall be regarded as the state of the input.  Both normal and inverted outputs shall be generated for each digital input channel.

### PULSE COUNTING

Pulses sensed by pulse counter modules shall be counted and stored in the integer data base, with a range of 0 to 32767.  Up to 125 pulses per second shall be counted per channel.  A pulse sample filter shall enable the digital input sampling to be delayed in 4 ms increments to filter out contact bounces.

### MOMENTARY PUSHBUTTON DETECTION

Momentary pushbutton actuations on digital inputs shall be captured and saved by background software as triggers for use by other modules.  The system shall detect any actuation greater than 10 milliseconds in duration.

### PULSE DURATION DETECTION

Background software shall measure and store the duration of digital inputs for interfacing with pulse duration type flow meters.  The system shall provide 10 millisecond resolution.

### SHAFT ENCODER COMPATIBILITY

When supplied shaft encoder software modules are employed, background software shall employ digital inputs in pairs to automatically provide compatibility with the following types of shaft encoders:  quadrature type;  count up/direction type; count up/count down type; short pulse count up/count down type.  The short pulse count up/down type shall employ interrupts to enable pulse rates in excess of 1Khz without missing any pulses.

## DIGITAL OUTPUTS

Each digital output board shall provide 4 normally open electromechanical relay output channels.  They shall be 120 VAC/24 VDC compatible with 10 amp UL/CSA contact rating into a resistive load.  Mechanical life shall exceed 10 million operations.  Relays shall require no more than 35 ma. to pull in.  How each channel is used  depends upon the specific software module used to interface to them as defined below.

### STANDARD ON/OFF CONTROL

When a relay output module calls for the relay, the relay shall energize; when the module calls for it to turn off, it shall turn off immediately.

### ALARM OUTPUT CONTROL

When an alarm output module calls for an output to turn on from a steady off state, the output shall turn on flashing every half second and remain flashing until acknowledged.  When acknowledged, the output shall assume a steady on or off state depending on the state of the alarm module’s alarm input state.  When the module’s lamp test input is on, the alarm output shall turn on steady then return to its former state when the lamp test input turns off.

### PULSE DURATION OUTPUTS

It shall be possible to designate any digital output as a pulse duration output, and to generate pulses on such outputs with user defined cycle period and duty cycle with a range of 15 seconds and resolution of 10 milliseconds.

## SERIAL PORTS

Two serial ports shall be provided in each unit.  Serial ports shall be independently configurable as to baud rate, word length, stop bits, parity, buffer length, communications protocol, etc., using the standard serial port settings.  Configuration shall be by communications setup module in the configuration file.  Communications protocols supported shall be RUG6, RUG9, ASCII, ALERT or MODBUS RTU protocol, minimum.  Loading of any software or configuration files shall use the CRC-secured RUG9 protocol.

### RS232 PORTS

An RS232 port shall be provided for local terminal/printer control, program loading, operating system loading, logged data dumping, interfacing to a local computer, or for general communications with local serial devices.  A second RS232 port shall be provided for general communications with external devices such as spread spectrum radios.  A standard cylindrical connector shall be provided enabling the RS232 ports to be connected to external devices such as PC-compatible computers using a standard cylindrical to DB9 cable adapter.  Cable connections shall be documented in the unit technical manual.

### MODEM

The second serial port shall be selectable under software control as RS232 or modem.  It shall be used for communicating with remotely located computers or other RTUs.  The RS232 port shall be compatible with spread spectrum radios, radios with integral modems, and with external high baud rate phone line modems.  In RS232 mode, the baud rates supported shall be the standard baud rated in the range of 50 to 19,200 baud.  The integral modem shall support 300 baud using the Bell 103 standard for use over phone lines or radio.  Audio interfaces shall be transformer isolated with 600 ohm line impedance.  An integral audio amplifier with a software adjustable 0 to 255 digital potentiometer adjustment range (nominal 0.0 to 3.0 V pk to pk) shall be provided on the transmitter channel to accommodate highly attenuated lines.  A radio transmitter key circuit using optical isolation shall also be provided.  Connection to the modem shall be via separate cylindrical jacks for the RS232 and audio/key line interfaces.  Additionally, a separate cylindrical jack shall be provided into which a stereo headset cable can be plugged to enable listening to the audio transmit and receive channels on left and right channels, respectively.  The audio interface shall use metal oxide varistor (MOV) and back to back zener diode lightning protection between signal lines.  The MOV shall be rated for 1200 amps surge current.

ALERT TONE COMPATIBILITY

In addition to the Bell compatible tone set, the unit shall be available with the ALERT compatible tone set.

## POWER INTERFACE

The unit shall operate from 12 VDC.  Input voltage tolerance shall be +/- 20%.  An internal resettable fuse shall protect the unit from over current.  Unit current draw shall be less than 2.0 ma. with all output relays off, loop supplies off and display backlight off.  An integral power failure and brownout detector shall be provided.  Diode isolation shall be provided to protect against external battery reverse connection.

## I/O CONNECTIONS

All I/O connections shall employ individual screw type terminals using the rising cage clamp design capable of accepting 14 AWG wire.  The terminals shall be removable in groups of 8 to 10 from PC board headers so that the unit can be changed out without removing field wires individually.

## ONBOARD DIAGNOSTICS

The onboard diagnostics shall measure, battery voltage, onboard temperature, and scan time.  Measurements shall be factory calibrated, requiring no field calibration for accurate measurements.  Calibration shall be retained in flash memory on the board and read at boot up.  The battery voltage measurement shall enable the unit to sense battery discharge before battery voltage falls below the brownout shutdown voltage.  Database statuses shall be provided for battery undervoltage.

## LOOP SUPPLY

A switching type regulated 24 VDC loop power supply shall boost bus voltage to supply up to 120 ma. for powering external 4-20 ma. transducers.  The supply shall be switched under software control to enable shutdown of transducers and periodic power up in low power solar applications.

## REFERENCE SUPPLY

A software switchable, regulated 5.0 volt reference supply shall be provided for powering unpowered instruments such as potentiometers.

# RTU SOFTWARE

## SECURITY SOFTWARE

Software shall be provided for verifying the integrity of the operating system and user configuration file on power application and immediately following file loading.  Failure of the code to pass its check shall cause the unit to suspend operation of that software and issue a message through the CPU serial port prompting for software re-installation.

## SCANNING SOFTWARE

All I/O scanning shall be done by operating system software without need for programmer attention.  Keyboard and serial port scanning shall use interrupts for fast response and to reduce scanning overhead.  Keyboard multi-digit user entries shall be captured by background software without affecting the running program.  Each entry shall be entered into a setpoint register immediately after the user hits the [ENTER] key at which time the new setpoint entry will take effect.

### VARIABLE TYPES AND RESOLUTION

The operating system shall support the following numeric types with the ranges specified:

TYPE		RANGE

Status		0 to 1

Integer		-32768 to +32767

Floating point 	1.7E38 to 2.9E-39

## COMMUNICATIONS SOFTWARE

### PORT BUFFERING

Each serial port shall have receive and transmit buffers of length set by the compiler based on compiler’s detected use of the port or based on the programmer’s setting.  Interrupt driven background software shall accomplish buffer filling and emptying using a ring buffer structure to minimize the possibility of missing data.  A continuous data rate of 9600 baud shall be supported.

### SERIAL PORT PARAMETER SETTING

Serial port parameter settings shall be set by a port setup module per port.  The following parameters shall be defined in the setup module:

Baud rate	Word length		Stop bits		Parity

Tone use	UART connection	Address		Protocol

Tx delay		Trigger to install		Buffer length

### CRC ERROR DETECTION

Background software shall accommodate message reception and transmission using CRC error checking.  Each message shall consist of a fixed length header portion and an optional variable length data section.  Background software shall generate CRC codes for outgoing messages, and shall check CRC codes for received messages.  Any received message having invalid CRC codes shall be discarded with no reply .

### COMMUNICATIONS WITH OTHER RTU’s

Upon reception of a message with correct unit address and correct CRC codes, background software shall take the action specified in the message and generate the proper response.  This action shall be transparent to the running program, except that the message reception and message type shall be made available to the program in the form of triggers.  Using built in message formats, it shall be possible to transfer analog measurements, setpoints, statuses, commands, totalizations, clock settings, etc. between a central computer and any or all remote units, and between remote units.  It shall be possible for messages to contain a mix of 16 bit integers, 32 bit integers, statuses, and 32 bit floating point numbers.  In addition to receiving messages having a unit’s address, it shall be possible for a unit to capture messages from one unit to another, both of which have different addresses than that of the receiving unit.  In this case, no reply will be generated.  A broadcast mode using address zero (0) shall be implemented whereby any unit having an array setup for address 0 shall capture data addressed to address 0 and not generate a reply.

### PEER TO PEER COMMUNICATIONS

It shall be possible for the unit to issue all commands supported by its formats except for memory loading and program run/stop commands by specifying destination unit address and message type.  Background software shall take care of generating the message, accepting the response, and transferring data between the port buffers and the pre-assigned databases.  Background software shall make message transfer status and result available to the program for use in accumulating statistics on link performance, and for notifying that requested data has been received.  Using these messages it shall be possible to transfer analog values, integers and statuses efficiently and securely between remote units with minimum numbers of messages necessary.

### STORE AND FORWARD OPERATION

The system shall support message store and forward operation so that stations out of range or otherwise out of communications visibility shall be able to communicate using intermediary RTU's.  The specific path each forwarded message is to take shall be specified at time of message initiation by the initiating station.  The path shall be contained in the message so that any receiving station can determine whether it is to forward the message, and to which station it is to forward the message, based entirely upon the contents of the message.  In this manner, the initiating station shall be capable of trying an alternate path to accommodate failed intermediary stations.  The unit shall be capable of forwarding through a path of as many as 3 intermediary stations, and of retrieving a reply through the identical reverse path.  In order that the a station shall be able to forward messages without a prior site visit or program change, it shall not be necessary for the programmer to include any code or modules other than normal communications setup for a unit to perform store and forwarding.

### UNIT ADDRESS RANGE

Each port shall have a two byte address kept in flash memory, enabling an address range of 1 to 65,000.

## PREPROGRAMMED MODULES

Instead of programming in the usual procedural sense, the RTU shall be configured using, as a minimum, the following modules by connecting the outputs of the modules contained in the databases, to the inputs of other module(s).  All the modules listed below shall be included in the operating system and supported by the support software such that no additional software shall have to be purchased or downloaded in order to obtain these functions.

I/O MODULES

Analog input

Anemometer

Digital input counter

Digital output alarm

Digital input

Digital output

Get user value

Message to display

Pulse duration input

Pulse duration output

Pulse to flow

Setpoint

Shaft Encoder Input

System  setup

MATH

Bits to Numeric

Constant

Cosine

Float to integer

Flow CipolletiRect

Flow AGA3

Flow container

Flow convert/dropout

Flow H flume

Flow Palmer-Bowlus

Flow Parshall

Flow Q=A*(H+B)**C

Flow trapez flume

Limit

Low pass filter

Mask integer

Numeric to bits

Numeric to string

Polynomial Nth order

Power

Sine

Square root

Tangent

Trigger to numeric

Y=A*B

Y=A-B

Y=A*B

Y=A/B

Y=A*B*C*D*E*F*G*H

Y=A*B+C*D+E*F+G*H

Y=A+B*C/D-E

Y=A+B*exp**(X+C)

Y=A+B*rand(1)

Y=A+B+C+D+E+F+G+H

Y=A+B+C+D-E-F-G-H

Y=abs(X)

Y=Log(X)

Y=Log10(X)

Y=MX+B

Y=sqrt(X)

Y=X^Z (power)

CONTROL

Alarm hi/low

AND gate

Backspin timer

Clear RAM

Counter

Count up/down rellover

Deadband

Delay timer

Exclusive OR

EventFIFOQueue

Flip flop

Flip flop RS

HOA

HOA2

Index value save

Intrusion

Latch float value

Latch integer value

Latch on bit change

Latch string

#### Lead lag seq4

Lookup switch

Mismatch latch

Off delay

On delay

OR gate

OR gate latched

PID

Poke

Poke many

Pulse generator

Pulse gen fast

Pump down controller

Pump up controller

Pump up/dn controller

Rate of change

Read realtime clock

Sequencer timed #2

Sequencer timed

Sequencer timed trigger

Sequencer up/down

Sequencer out (expander)

Set realtime clock

Snapshot Count

String switch

String switch by bits

Sync to RTC

Toggle

Trigger every X seconds

Trigger generator

Trigger on change

Trigger on change many

Trigger on keymany

Trigger on realtime clock

Trigger on bit then clear

Value test

Value test trig

STATISTICS

Average value

Log many

Max value

Min value

Read from Log Many

Totalize event

Totalize flow

Totalize time

COMMUNICATIONS

Communications setup

Com watch

Cycle display

Get string from port

Poll

Quiescent controller

Send Alert Data

Send string to port

Sequenced poller

Send string to port

StringMid

Trigger on receive

MAJOR BLOCKS

Display definition

Ladder logic

Modbus slave

R6/R9 CRC secure comm

Table setup

Watch window debugger

## LADDER LOGIC

The RTU shall enable the programmer to use ladder logic to implement any control strategies not covered by preprogrammed modules.  Each rung shall have a minimum of 7 input contacts and a single coil output.  The programmer shall be able to refer to contacts and coils by user defined names.  Input contacts shall be designated as either normally open or normally closed.  Each coil shall have independent ON delay and OFF delay entries that can be left blank for no delay, or may have either a constant or database variable to control the delay with one second resolution.

## EVENT TIMING

Events shall be timed by either the realtime clock with one second resolution, or by individual countdown registers that are decremented each 1.0 second.

## FAULT TRAPPING

The unit shall test for potential math errors as it executes the modules and return the most reasonable result (MAXVALUE or MINVALUE) instead of allowing run time errors.  If any unrecoverable run time error occurs, the unit shall halt operation and allow the watchdog timer to reboot the system.

## CLOCK SETTING

Software shall enable personnel to examine and set the realtime clock/calendar using an English language query and response method.  It shall also be possible using a global RTC command for one site to set all the realtime clocks in the system.

## DISPLAY CONTROL

Displays shall be accessed by hitting the [ENTER] key to traverse to the next display in the list of displays defined for the project.  After the last display in the list is accessed, the list shall roll back to the first display in the list.  At any time, the operator shall be able to hit the [-] key to obtain a menu of displays in the project from which he may choose the next one to be displayed.  Displays shall be refreshed at a user specified time based upon a user designated trigger.  The trigger can be a time tick, an event, a reception of a message, etc.  A separate display list shall be kept for the LCD display and for each serial port in the project that is in ASCII mode.

## DISPLAY FORMAT DEFINITION

Displays shall be defined by typing in the data to be presented using the Windows compatible program that is used to configure the RTU.  Data to be shown on the RTU’s LCD or ASCII serial port(s) shall be presented exactly as entered into the Windows configuration program.  Where dynamic data are to be shown, the user shall only have to type in ‘@’ symbols to specify the size, format and location of the variable field, and then drag in the variable that is to be displayed in the specified field.  The RTU shall present the variable data in real time in the format and location entered as example by the user.

## WATCH WINDOW DEBUGGING AID

Support software shall include a watch window that shall enable the programmer to drag up to 5 items from the RTU’s databases and observe their current values/states/string contents in realtime with once per second automatic updates.  He shall be able to double click on a value in the watch window to engage a poke mode whereby the programmer can jam a value into a variable in the running RTU in place of the result that would normally be present.  In this manner, the programmer shall be able to substitute a value for any input or calculated result to observe the unit’s response without having to connect transducer simulators or other external signal generators.

## DOCUMENTATION GENERATOR

Support software shall include a documentation generator that, when triggered, will generate an ASCII file that completely documents the project’s design in easily read text.  Items to be documented shall be selectively enabled and shall include at least the following:

- Operating instructions

- I/O setup by channel

- Software module setup

- Display formats

- Telemetry array formats

- Ladder logic setup

- Table setup

- Database listings

- Database variable cross references

# PERFORMANCE

## I/O SCANNING

Background software shall scan analog and digital inputs at the rates specified above.  For a nominal control application, the RTU shall accomplish all its scanning tasks in less than 0.05 second.

## COMMUNICATIONS RESPONSE TIME

The unit shall issue a response to a CRC secured message in less than 60 milliseconds.  Provisions shall be made whereby the delay from transmission tone on to actual output of data is adjustable over the range of 10 to 3277 milliseconds in increments of 100 milliseconds to accommodate transmitter turnon delay, receiver acquisition time and receiving modem acquisition time.  The specification of the tone turnon delay shall be specified in the communications definition module held in flash memory.  Assuming a transfer of 16 digital inputs, the following response times shall be met, including time to request a transfer and receive and decode the transfer:

300 baud:      9 transfers in 10 seconds

9600 baud:     90 transfers in 10 seconds

Assuming a transfer of 8 analog values, the following response times shall be met:

300 baud:      6 transfers in 10 seconds

9600 baud:     67 transfers in 10 seconds

## COMMUNICATIONS SECURITY

The CRC error detection technique shall provide a probability of acceptance of an erroneous message of 1.0 E-14.  It shall also reject all burst errors of 16 bits or less.

## KEYBOARD RESPONSE TIME

The unit shall respond to operator keystrokes in less than 20 milliseconds.

# ENVIRONMENTAL COMPATIBILITY

## ENCLOSURE

The unit housing shall be constructed of 16 gauge steel with integral threaded holes capable of securing the RTU circuit card and back plate, and capable of being mounted on a standard 7 X 35 mm. DIN rail.  Enclosure size shall be no larger than 4.6 inches wide by 3.6 inches high by 1.25 inches deep.  The steel display enclosure shall also house the keyboard, LCD display, and support electronics.  Enclosure finish shall be powder-coated.

## TEMPERATURE RANGE

The unit shall operate over an ambient temperature range of -40 to +85 degrees Centigrade.  The display shall operate over a range of -20 to +65 degrees Centigrade and shall survive a range of -40 to +70 degrees Centigrade.  No cooling fans or air circulation shall be required for normal unit operation over the temperature range specified.

# TESTING

Each unit shall be thoroughly tested at the factory before shipment to ascertain that all functions are operating normally.  Each unit shall additionally be burned in for a minimum of 24 hours to reveal and correct infant mortality failures before shipment.

# DOCUMENTATION

Documentation shall be deliverable on CD or be available for download at no charge from the manufacturer’s web site.  The documentation shall include a complete technical manual of at least 210 pages that provides connection examples for all I/O connections and describes background software, communications formats, and the software modules.

# WARRANTY AND REPAIR

The unit shall be warranted for a period of 1 year from date of delivery, including parts and labor.  The manufacturer shall guarantee that any failed unit shall be repaired and shipped within 24 hours of receipt by the factory.